## Modbus
Stav rele / State of relays
0x01 | 0x0000 | 0x0008
Externi vstupy / External inputs
0x02 | 0x0000 | 0x0008
Identifikace / Indentification
0x11
Výkonné příkazy / Do action
0x05 | 0x0000 | 0xFF00 | 0 |  |  | Zeroed value on display.
0x05 | 0x0001 | 0xFF00 | 1 |  |  | Cancel display resetting (Tare clear)
0x05 | 0x0002 | 0xFF00 | 2 |  |  | Minimum and maximum clear
0x05 | 0x0003 | 0xFF00 | 3 |  |  | Clear memory of measured datas
0x05 | 0x0004 | 0xFF00 | 4 |  |  | Measure leads resistance
0x05 | 0x0005 | 0xFF00 | 5 |  |  | Meas low end of range of linear potentiometer
0x05 | 0x0006 | 0xFF00 | 6 |  |  | Meas high end of range of linear potentiometer
Vyčtení naměřených a vypočtených hodnot / Reading of measured or evaluated values
0x04 | 0x0004 | 0x0002 | 30004 | float | FIL.A
0x04 | 0x0006 | 0x0002 | 30006 | float | M. FN.
0x04 | 0x0008 | 0x0002 | 30008 | float | MIN.
0x04 | 0x000A | 0x0002 | 30010 | float | MAX.
0x04 | 0x0018 | 0x0002 | 30024 | float | TARA
0x04 | 0x001C | 0x0002 | 30028 | float | ST. K.
Vyčtení hodnot z menu / Reading menu item values
0x03 | 0x0008 | 0x0001 | 40008 | List | VST. – KONF. – M/S | Measuring rate | 0= 40.0, 1= 20.0, 2= 10.0, 3= 5.0, 4= 2.0, 5= 1.0, 6= 0.5, 7= 0.2, 8= 0.1
0x03 | 0x000A | 0x0001 | 40010 | List | VST. – KONF. – TYP | Instrument type | 0=DC, 1=PM, 2=OHM, 3=Pt, 4=Ni, 5=TC, 6=DU, 7=Cu
0x03 | 0x000C | 0x0001 | 40012 | List | VST. – KONF. – MOD | Instrument mode | 0= 60, 1= 150, 2= 300, 3=1200, 4=i0-5, 5=0-20, 6=4-20, 7=u0-2, 8=u0-5, 9=0-10, 10=0-40, 11= 0.1, 12= 1.0, 13= 10.0, 14=100.0, 15=EU0.1, 16=EU0.5, 17=EU1.0, 18=US0.1, 19=5- 1, 20=6- 1, 21=5-10, 22=6-10, 23=TC B, 24=TC E, 25=TC J, 26=TC K, 27=TC N, 28=TC R, 29=TC S, 30=TC T, 31=L.POT., 32=100V, 33=250V, 34=500V, 35=0.10A, 36=0.25A, 37=0.50A, 38=2.00A, 39=5.00A, 40=R. 50, 41=R.100, 42=8-50, 43=8-0.1, 44=6-50, 45=6-0.1, 46=TC L, 47=Er 4
0x03 | 0x000E | 0x0001 | 40014 | List | VST. – KONF. – PRIP. | Sensor connection | 0=INT.1, 1=INT.2, 2=EXT.1, 3=EXT.2, 4=2-W., 5=3-W., 6=4-W.
0x03 | 0x0010 | 0x0002 | 40016 | Float | VST. – KONF. – T. S.K. | CJC temperature | 0..99
0x03 | 0x0012 | 0x0002 | 40018 | Float | VST. – KONF. – POS. | Offset value | 0..40
0x03 | 0x0014 | 0x0001 | 40020 | Char | VST. – KONF. – VED. | 3L. GRID. Calculation of 3-phase power output - the value is calculated with the assumption of a balanced demand in all phases - for P, S Q the value is multiplied by 3 | ..
0x03 | 0x0022 | 0x0001 | 40034 | List | VST. – E. VS. – EX. 1 | Setting auxiliary input 1 | 0=OFF, 1=HOLD, 2=LO. K., 3=B.PAS., 4=TARE, 5=C. TA., 6=C. M.M., 7=SAVE, 8=C. ME.
0x03 | 0x0024 | 0x0001 | 40036 | List | VST. – E. VS. – EX. 2 | Setting auxiliary input 2 | 0=OFF, 1=HOLD, 2=LO. K., 3=B.PAS., 4=TARE, 5=C. TA., 6=C. M.M., 7=SAVE, 8=C. ME.
0x03 | 0x0026 | 0x0001 | 40038 | List | VST. – E. VS. – EX. 3 | Setting auxiliary input 3 | 0=OFF, 1=HOLD, 2=LO. K., 3=B.PAS., 4=TARE, 5=C. TA., 6=C. M.M., 7=SAVE, 8=C. ME.
0x03 | 0x0028 | 0x0001 | 40040 | List | VST. – E. VS. – M. HO. | Range of instrument blocation | 0=DISP., 1=D. A.O., 2=D.A.O.L., 3=ALL
0x03 | 0x002A | 0x0001 | 40042 | List | VST. – KLAV. – LEFT – FN. L. | Function setting for key LEFT | 0=NO, 1=C. M.M., 2=C. TA., 3=MENU, 4=TMP.V., 5=TARE, 6=SAVE, 7=C. ME.
0x03 | 0x002C | 0x0001 | 40044 | List | VST. – KLAV. – LEFT – DO. L. | Choice of value for temporary show | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x002E | 0x0001 | 40046 | List | VST. – KLAV. – LEFT – MN. L. | Choice of menu item | 0=L. 1, 1=L. 2, 2=L. 3, 3=L. 4
0x03 | 0x0030 | 0x0001 | 40048 | List | VST. – KLAV. – DOWN – FN. D. | Function setting for key DOWN | 0=NO, 1=C. M.M., 2=C. TA., 3=MENU, 4=TMP.V., 5=TARE, 6=SAVE, 7=C. ME.
0x03 | 0x0032 | 0x0001 | 40050 | List | VST. – KLAV. – DOWN – DO. D. | Choice of value for temporary show | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x0034 | 0x0001 | 40052 | List | VST. – KLAV. – DOWN – MN. D. | Choice of menu item | 0=L. 1, 1=L. 2, 2=L. 3, 3=L. 4
0x03 | 0x0036 | 0x0001 | 40054 | List | VST. – KLAV. – UP – FN. U. | Function setting for key UP | 0=NO, 1=C. M.M., 2=C. TA., 3=MENU, 4=TMP.V., 5=TARE, 6=SAVE, 7=C. ME.
0x03 | 0x0038 | 0x0001 | 40056 | List | VST. – KLAV. – UP – DO. U. | Choice of value for temporary show | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x003A | 0x0001 | 40058 | List | VST. – KLAV. – UP – MN. U. | Choice of menu item | 0=L. 1, 1=L. 2, 2=L. 3, 3=L. 4
0x03 | 0x003C | 0x0001 | 40060 | List | VST. – KLAV. – ENTR. – FN. E. | Function setting for key ENTER | 0=NO, 1=C. M.M., 2=C. TA., 3=MENU, 4=TMP.V., 5=TARE, 6=SAVE, 7=C. ME.
0x03 | 0x003E | 0x0001 | 40062 | List | VST. – KLAV. – ENTR. – DO. E. | Choice of value for temporary show | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x0040 | 0x0001 | 40064 | List | VST. – KLAV. – ENTR. – MN. E. | Choice of menu item | 0=L. 1, 1=L. 2, 2=L. 3, 3=L. 4
0x03 | 0x0042 | 0x0002 | 40066 | Float | KAN. – K. A – NAS.A – MIN.A | Value corresponding w/ minimum value of input range | -1999..9999
0x03 | 0x0044 | 0x0002 | 40068 | Float | KAN. – K. A – NAS.A – MAX.A | Value corresponding w/ maximum value of input range | -1999..9999
0x03 | 0x0046 | 0x0002 | 40070 | Float | KAN. – K. A – NAS.A – P.T. A | Handy set value of tare | -1999..9999
0x03 | 0x0048 | 0x0001 | 40072 | List | KAN. – K. A – FIL. – M. F.A | Filter mode | 0=NO, 1=AVER., 2=FLOA., 3=EXP., 4=ROUN.
0x03 | 0x004A | 0x0002 | 40074 | Float | KAN. – K. A – FIL. – K. FA | Filter constant | 0,001..9999
0x03 | *0x004A | 0x0002 | 40074 | Float | KAN. – K. A – FIL. – K. FA | Filter constant | 2..Filter2Delka
0x03 | *0x004A | 0x0002 | 40074 | Float | KAN. – K. A – FIL. – K. FA | Filter constant | 2..Filter3Delka
0x03 | 0x0050 | 0x0001 | 40080 | List | KAN. – K. A – ZOB.A | Projection format | 0=0000., 1=000.o, 2=00.oo, 3=0.ooo, 4=FL. P.
0x03 | 0x0058 | 0x0001 | 40088 | List | KAN. – MAT.F. – MAT.F. | Mathematic function select | 0=OFF, 1=MULT., 2=1/MU., 3=LOG., 4=EXP., 5=POW., 6=ROOT, 7=SIN
0x03 | 0x005A | 0x0002 | 40090 | Float | KAN. – MAT.F. – KO. A | Constant A | -1999..9999
0x03 | 0x005C | 0x0002 | 40092 | Float | KAN. – MAT.F. – KO. B | Constant B | -1999..9999
0x03 | 0x005E | 0x0002 | 40094 | Float | KAN. – MAT.F. – KO. C | Constant C | -1999..9999
0x03 | 0x0060 | 0x0002 | 40096 | Float | KAN. – MAT.F. – KO. D | Constant D | -1999..9999
0x03 | 0x0062 | 0x0002 | 40098 | Float | KAN. – MAT.F. – KO. E | Constant E | -1999..9999
0x03 | 0x0064 | 0x0002 | 40100 | Float | KAN. – MAT.F. – KO. F | Constant F | -1999..9999
0x03 | 0x0066 | 0x0001 | 40102 | List | KAN. – MAT.F. – ZOB.M | Projection format | 0=0000., 1=000.o, 2=00.oo, 3=0.ooo, 4=FL. P.
0x03 | 0x006E | 0x0001 | 40110 | List | KAN. – MI.MA. – V. M.M. | Input value for minimum and maximum | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x0084 | 0x0002 | 40132 | Float | VYST. – PAM. – SPUS. | Size of pretrigger area of memory | 0..100
0x03 | 0x0086 | 0x0001 | 40134 | List | VYST. – LIM. – L. 1 – VS.L.1 | Input value for limit 1 | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x0088 | 0x0001 | 40136 | List | VYST. – LIM. – L. 1 – MO.L.1 | Mode of controling limit | 0=HYST., 1=FR.TO, 2=DOSE
0x03 | 0x008A | 0x0001 | 40138 | List | VYST. – LIM. – L. 1 – TY.L.1 | Limit type | 0=CLOS., 1=OPEN
0x03 | 0x008C | 0x0002 | 40140 | Float | VYST. – LIM. – L. 1 – M. L.1 | Limit value | -1999..9999
0x03 | 0x008E | 0x0002 | 40142 | Float | VYST. – LIM. – L. 1 – H. L.1 | Hysteresis | 0..9999
0x03 | *0x008C | 0x0002 | 40140 | Float | VYST. – LIM. – L. 1 – ZA.L.1 | Limit value | -1999..9999
0x03 | *0x008E | 0x0002 | 40142 | Float | VYST. – LIM. – L. 1 – VY.L.1 | Hysteresis | -1999..9999
0x03 | *0x008E | 0x0002 | 40142 | Float | VYST. – LIM. – L. 1 – PE.L.1 | Hysteresis | 0,001..9999
0x03 | 0x0096 | 0x0002 | 40150 | Float | VYST. – LIM. – L. 1 – C. L.1 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x03 | 0x0098 | 0x0001 | 40152 | List | VYST. – LIM. – L. 2 – VS.L.2 | Input value for limit 2 | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x009A | 0x0001 | 40154 | List | VYST. – LIM. – L. 2 – MO.L.2 | Mode of controling limit | 0=HYST., 1=FR.TO, 2=DOSE
0x03 | 0x009C | 0x0001 | 40156 | List | VYST. – LIM. – L. 2 – TY.L.2 | Limit type | 0=CLOS., 1=OPEN
0x03 | 0x009E | 0x0002 | 40158 | Float | VYST. – LIM. – L. 2 – M. L.2 | Limit value | -1999..9999
0x03 | 0x00A0 | 0x0002 | 40160 | Float | VYST. – LIM. – L. 2 – H. L.2 | Hysteresis | 0..9999
0x03 | *0x009E | 0x0002 | 40158 | Float | VYST. – LIM. – L. 2 – ZA.L.2 | Limit value | -1999..9999
0x03 | *0x00A0 | 0x0002 | 40160 | Float | VYST. – LIM. – L. 2 – VY.L.2 | Hysteresis | -1999..9999
0x03 | *0x00A0 | 0x0002 | 40160 | Float | VYST. – LIM. – L. 2 – PE.L.2 | Hysteresis | 0,001..9999
0x03 | 0x00A8 | 0x0002 | 40168 | Float | VYST. – LIM. – L. 2 – C. L.2 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x03 | 0x00AA | 0x0001 | 40170 | List | VYST. – LIM. – L. 3 – VS.L.3 | Input value for limit 3 | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x00AC | 0x0001 | 40172 | List | VYST. – LIM. – L. 3 – MO.L.3 | Mode of controling limit | 0=HYST., 1=FR.TO, 2=DOSE
0x03 | 0x00AE | 0x0001 | 40174 | List | VYST. – LIM. – L. 3 – TY.L.3 | Limit type | 0=CLOS., 1=OPEN
0x03 | 0x00B0 | 0x0002 | 40176 | Float | VYST. – LIM. – L. 3 – M. L.3 | Limit value | -1999..9999
0x03 | 0x00B2 | 0x0002 | 40178 | Float | VYST. – LIM. – L. 3 – H. L.3 | Hysteresis | 0..9999
0x03 | *0x00B0 | 0x0002 | 40176 | Float | VYST. – LIM. – L. 3 – ZA.L.3 | Limit value | -1999..9999
0x03 | *0x00B2 | 0x0002 | 40178 | Float | VYST. – LIM. – L. 3 – VY.L.3 | Hysteresis | -1999..9999
0x03 | *0x00B2 | 0x0002 | 40178 | Float | VYST. – LIM. – L. 3 – PE.L.3 | Hysteresis | 0,001..9999
0x03 | 0x00BA | 0x0002 | 40186 | Float | VYST. – LIM. – L. 3 – C. L.3 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x03 | 0x00BC | 0x0001 | 40188 | List | VYST. – LIM. – L. 4 – VS.L.4 | Input value for limit 4 | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x00BE | 0x0001 | 40190 | List | VYST. – LIM. – L. 4 – MO.L.4 | Mode of controling limit | 0=HYST., 1=FR.TO, 2=DOSE
0x03 | 0x00C0 | 0x0001 | 40192 | List | VYST. – LIM. – L. 4 – TY.L.4 | Limit type | 0=CLOS., 1=OPEN
0x03 | 0x00C2 | 0x0002 | 40194 | Float | VYST. – LIM. – L. 4 – M. L.4 | Limit value | -1999..9999
0x03 | 0x00C4 | 0x0002 | 40196 | Float | VYST. – LIM. – L. 4 – H. L.4 | Hysteresis | 0..9999
0x03 | *0x00C2 | 0x0002 | 40194 | Float | VYST. – LIM. – L. 4 – ZA.L.4 | Limit value | -1999..9999
0x03 | *0x00C4 | 0x0002 | 40196 | Float | VYST. – LIM. – L. 4 – VY.L.4 | Hysteresis | -1999..9999
0x03 | *0x00C4 | 0x0002 | 40196 | Float | VYST. – LIM. – L. 4 – PE.L.4 | Hysteresis | 0,001..9999
0x03 | 0x00CC | 0x0002 | 40204 | Float | VYST. – LIM. – L. 4 – C. L.4 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x03 | 0x00CE | 0x0001 | 40206 | List | VYST. – DATA – BAUD | Transfer rate | 0= 0.6, 1= 1.2, 2= 2.4, 3= 4.8, 4= 9.6, 5= 19.2, 6= 38.4, 7= 57.6, 8=115.2, 9=230.4
0x03 | 0x00D0 | 0x0002 | 40208 | Float | VYST. – DATA – ADR. | Instrument address | 0..31
0x03 | 0x00D6 | 0x0001 | 40214 | List | VYST. – DATA – PROT. | Communication protocol | 0=ASCI., 1=M.BUS, 2=MODB.
0x03 | 0x00D8 | 0x0001 | 40216 | List | VYST. – ANAL. – VS.A.V. | Input value for analog output | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x00DA | 0x0001 | 40218 | List | VYST. – ANAL. – TY.A.V. | Type | 0=0-20, 1=Er4T, 2=4-2T, 3=Er 4, 4=4-20, 5=i0-5, 6=u0-2, 7=u0-5, 8=0-10, 9=+-10
0x03 | 0x00DC | 0x0002 | 40220 | Float | VYST. – ANAL. – MI.A.V. | Minimum display value corresponding with bottom value of selected A.O. range | -1999..9999
0x03 | 0x00DE | 0x0002 | 40222 | Float | VYST. – ANAL. – MA.A.V. | Maximum display value corresponding with top value of selected A.O. range | -1999..9999
0x03 | 0x00E0 | 0x0001 | 40224 | List | VYST. – DISP. – TRV. | Value to be permanent displayed | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x03 | 0x00E2 | 0x0001 | 40226 | List | VYST. – DISP. – BAR.0 | Color of value display | 0=RED, 1=GRN., 2=ORAN.
0x03 | 0x00E4 | 0x0002 | 40228 | Float | VYST. – DISP. – D.L. 1. | Value of color 0 / 1 | -1999..9999
0x03 | 0x00E6 | 0x0001 | 40230 | List | VYST. – DISP. – BAR.1 | Color of value display when relay 1 is on | 0=RED, 1=GRN., 2=ORAN.
0x03 | 0x00E8 | 0x0002 | 40232 | Float | VYST. – DISP. – D.L. 2. | Value of color 1 / 2 | -1999..9999
0x03 | 0x00EA | 0x0001 | 40234 | List | VYST. – DISP. – BAR.2 | Display and main bargraph color when second relay is ON. First relay is not sigificant. | 0=RED, 1=GRN., 2=ORAN.
0x03 | 0x00EC | 0x0001 | 40236 | List | VYST. – DISP. – JAS | Brightness of displey | 0= 0%, 1= 25%, 2= 50%, 3= 75%, 4=100%
0x03 | 0x00FA | 0x0001 | 40250 | List | SERV. – JAZ. | Language variation of menu | 0=CZE., 1=ENGL.
Nastavení hodnot menu / Setting menu item values
0x06 | 0x0008 | 0x0200XX | 40008 | List | VST. – KONF. – M/S | Measuring rate | 0= 40.0, 1= 20.0, 2= 10.0, 3= 5.0, 4= 2.0, 5= 1.0, 6= 0.5, 7= 0.2, 8= 0.1
0x06 | 0x000A | 0x0200XX | 40010 | List | VST. – KONF. – TYP | Instrument type | 0=DC, 1=PM, 2=OHM, 3=Pt, 4=Ni, 5=TC, 6=DU, 7=Cu
0x06 | 0x000C | 0x0200XX | 40012 | List | VST. – KONF. – MOD | Instrument mode | 0= 60, 1= 150, 2= 300, 3=1200, 4=i0-5, 5=0-20, 6=4-20, 7=u0-2, 8=u0-5, 9=0-10, 10=0-40, 11= 0.1, 12= 1.0, 13= 10.0, 14=100.0, 15=EU0.1, 16=EU0.5, 17=EU1.0, 18=US0.1, 19=5- 1, 20=6- 1, 21=5-10, 22=6-10, 23=TC B, 24=TC E, 25=TC J, 26=TC K, 27=TC N, 28=TC R, 29=TC S, 30=TC T, 31=L.POT., 32=100V, 33=250V, 34=500V, 35=0.10A, 36=0.25A, 37=0.50A, 38=2.00A, 39=5.00A, 40=R. 50, 41=R.100, 42=8-50, 43=8-0.1, 44=6-50, 45=6-0.1, 46=TC L, 47=Er 4
0x06 | 0x000E | 0x0200XX | 40014 | List | VST. – KONF. – PRIP. | Sensor connection | 0=INT.1, 1=INT.2, 2=EXT.1, 3=EXT.2, 4=2-W., 5=3-W., 6=4-W.
0x10 | 0x0010 | 0x000204EEMMMMMM | 40016 | Float | VST. – KONF. – T. S.K. | CJC temperature | 0..99
0x10 | 0x0012 | 0x000204EEMMMMMM | 40018 | Float | VST. – KONF. – POS. | Additional resistance in probe | 0..40
0x06 | 0x0022 | 0x0200XX | 40034 | List | VST. – E. VS. – EX. 1 | Setting auxiliary input 1 | 0=OFF, 1=HOLD, 2=LO. K., 3=B.PAS., 4=TARE, 5=C. TA., 6=C. M.M., 7=SAVE, 8=C. ME.
0x06 | 0x0024 | 0x0200XX | 40036 | List | VST. – E. VS. – EX. 2 | Setting auxiliary input 2 | 0=OFF, 1=HOLD, 2=LO. K., 3=B.PAS., 4=TARE, 5=C. TA., 6=C. M.M., 7=SAVE, 8=C. ME.
0x06 | 0x0026 | 0x0200XX | 40038 | List | VST. – E. VS. – EX. 3 | Setting auxiliary input 3 | 0=OFF, 1=HOLD, 2=LO. K., 3=B.PAS., 4=TARE, 5=C. TA., 6=C. M.M., 7=SAVE, 8=C. ME.
0x06 | 0x0028 | 0x0200XX | 40040 | List | VST. – E. VS. – M. HO. | Range of instrument blocation | 0=DISP., 1=D. A.O., 2=D.A.O.L., 3=ALL
0x06 | 0x002A | 0x0200XX | 40042 | List | VST. – KLAV. – LEFT – FN. L. | Function setting for key LEFT | 0=NO, 1=C. M.M., 2=C. TA., 3=MENU, 4=TMP.V., 5=TARE, 6=SAVE, 7=C. ME.
0x06 | 0x002C | 0x0200XX | 40044 | List | VST. – KLAV. – LEFT – DO. L. | Choice of value for temporary show | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x002E | 0x0200XX | 40046 | List | VST. – KLAV. – LEFT – MN. L. | Choice of menu item | 0=L. 1, 1=L. 2, 2=L. 3, 3=L. 4
0x06 | 0x0030 | 0x0200XX | 40048 | List | VST. – KLAV. – DOWN – FN. D. | Function setting for key DOWN | 0=NO, 1=C. M.M., 2=C. TA., 3=MENU, 4=TMP.V., 5=TARE, 6=SAVE, 7=C. ME.
0x06 | 0x0032 | 0x0200XX | 40050 | List | VST. – KLAV. – DOWN – DO. D. | Choice of value for temporary show | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x0034 | 0x0200XX | 40052 | List | VST. – KLAV. – DOWN – MN. D. | Choice of menu item | 0=L. 1, 1=L. 2, 2=L. 3, 3=L. 4
0x06 | 0x0036 | 0x0200XX | 40054 | List | VST. – KLAV. – UP – FN. U. | Function setting for key UP | 0=NO, 1=C. M.M., 2=C. TA., 3=MENU, 4=TMP.V., 5=TARE, 6=SAVE, 7=C. ME.
0x06 | 0x0038 | 0x0200XX | 40056 | List | VST. – KLAV. – UP – DO. U. | Choice of value for temporary show | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x003A | 0x0200XX | 40058 | List | VST. – KLAV. – UP – MN. U. | Choice of menu item | 0=L. 1, 1=L. 2, 2=L. 3, 3=L. 4
0x06 | 0x003C | 0x0200XX | 40060 | List | VST. – KLAV. – ENTR. – FN. E. | Function setting for key ENTER | 0=NO, 1=C. M.M., 2=C. TA., 3=MENU, 4=TMP.V., 5=TARE, 6=SAVE, 7=C. ME.
0x06 | 0x003E | 0x0200XX | 40062 | List | VST. – KLAV. – ENTR. – DO. E. | Choice of value for temporary show | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x0040 | 0x0200XX | 40064 | List | VST. – KLAV. – ENTR. – MN. E. | Choice of menu item | 0=L. 1, 1=L. 2, 2=L. 3, 3=L. 4
0x10 | 0x0042 | 0x000204EEMMMMMM | 40066 | Float | KAN. – K. A – NAS.A – MIN.A | Scale | -1999..9999
0x10 | 0x0044 | 0x000204EEMMMMMM | 40068 | Float | KAN. – K. A – NAS.A – MAX.A | Value corresponding w/ maximum value of input range | -1999..9999
0x10 | 0x0046 | 0x000204EEMMMMMM | 40070 | Float | KAN. – K. A – NAS.A – P.T. A | Handy set value of tare | -1999..9999
0x06 | 0x0048 | 0x0200XX | 40072 | List | KAN. – K. A – FIL. – M. F.A | Filter mode | 0=NO, 1=AVER., 2=FLOA., 3=EXP., 4=ROUN.
0x10 | 0x004A | 0x000204EEMMMMMM | 40074 | Float | KAN. – K. A – FIL. – K. FA | Filter constant | 0,001..9999
0x10 | *0x004A | 0x000204EEMMMMMM | 40074 | Float | KAN. – K. A – FIL. – K. FA | Filter constant | 2..Filter2Delka
0x10 | *0x004A | 0x000204EEMMMMMM | 40074 | Float | KAN. – K. A – FIL. – K. FA | Filter constant | 2..Filter3Delka
0x06 | 0x0050 | 0x0200XX | 40080 | List | KAN. – K. A – ZOB.A | Projection format | 0=0000., 1=000.o, 2=00.oo, 3=0.ooo, 4=FL. P.
0x06 | 0x0058 | 0x0200XX | 40088 | List | KAN. – MAT.F. – MAT.F. | Mathematic function select | 0=OFF, 1=MULT., 2=1/MU., 3=LOG., 4=EXP., 5=POW., 6=ROOT, 7=SIN
0x10 | 0x005A | 0x000204EEMMMMMM | 40090 | Float | KAN. – MAT.F. – KO. A | Constant A | -1999..9999
0x10 | 0x005C | 0x000204EEMMMMMM | 40092 | Float | KAN. – MAT.F. – KO. B | Constant B | -1999..9999
0x10 | 0x005E | 0x000204EEMMMMMM | 40094 | Float | KAN. – MAT.F. – KO. C | Constant C | -1999..9999
0x10 | 0x0060 | 0x000204EEMMMMMM | 40096 | Float | KAN. – MAT.F. – KO. D | Constant D | -1999..9999
0x10 | 0x0062 | 0x000204EEMMMMMM | 40098 | Float | KAN. – MAT.F. – KO. E | Constant E | -1999..9999
0x10 | 0x0064 | 0x000204EEMMMMMM | 40100 | Float | KAN. – MAT.F. – KO. F | Constant F | -1999..9999
0x06 | 0x0066 | 0x0200XX | 40102 | List | KAN. – MAT.F. – ZOB.M | Projection format | 0=0000., 1=000.o, 2=00.oo, 3=0.ooo, 4=FL. P.
0x06 | 0x006E | 0x0200XX | 40110 | List | KAN. – MI.MA. – V. M.M. | Input value for minimum and maximum | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x10 | 0x0084 | 0x000204EEMMMMMM | 40132 | Float | VYST. – PAM. – SPUS. | Size of pretrigger area of memory | 0..100
0x06 | 0x0086 | 0x0200XX | 40134 | List | VYST. – LIM. – L. 1 – VS.L.1 | Input value for limit 1 | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x0088 | 0x0200XX | 40136 | List | VYST. – LIM. – L. 1 – MO.L.1 | Mode of controling limit | 0=HYST., 1=FR.TO, 2=DOSE
0x06 | 0x008A | 0x0200XX | 40138 | List | VYST. – LIM. – L. 1 – TY.L.1 | Limit type | 0=CLOS., 1=OPEN
0x10 | 0x008C | 0x000204EEMMMMMM | 40140 | Float | VYST. – LIM. – L. 1 – M. L.1 | Limit value | -1999..9999
0x10 | 0x008E | 0x000204EEMMMMMM | 40142 | Float | VYST. – LIM. – L. 1 – H. L.1 | Hysteresis | 0..9999
0x10 | *0x008C | 0x000204EEMMMMMM | 40140 | Float | VYST. – LIM. – L. 1 – ZA.L.1 | Limit value | -1999..9999
0x10 | *0x008E | 0x000204EEMMMMMM | 40142 | Float | VYST. – LIM. – L. 1 – VY.L.1 | Hysteresis | -1999..9999
0x10 | *0x008E | 0x000204EEMMMMMM | 40142 | Float | VYST. – LIM. – L. 1 – PE.L.1 | Hysteresis | 0,001..9999
0x10 | 0x0096 | 0x000204EEMMMMMM | 40150 | Float | VYST. – LIM. – L. 1 – C. L.1 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x06 | 0x0098 | 0x0200XX | 40152 | List | VYST. – LIM. – L. 2 – VS.L.2 | Input value for limit 2 | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x009A | 0x0200XX | 40154 | List | VYST. – LIM. – L. 2 – MO.L.2 | Mode of controling limit | 0=HYST., 1=FR.TO, 2=DOSE
0x06 | 0x009C | 0x0200XX | 40156 | List | VYST. – LIM. – L. 2 – TY.L.2 | Limit type | 0=CLOS., 1=OPEN
0x10 | 0x009E | 0x000204EEMMMMMM | 40158 | Float | VYST. – LIM. – L. 2 – M. L.2 | Limit value | -1999..9999
0x10 | 0x00A0 | 0x000204EEMMMMMM | 40160 | Float | VYST. – LIM. – L. 2 – H. L.2 | Hysteresis | 0..9999
0x10 | *0x009E | 0x000204EEMMMMMM | 40158 | Float | VYST. – LIM. – L. 2 – ZA.L.2 | Limit value | -1999..9999
0x10 | *0x00A0 | 0x000204EEMMMMMM | 40160 | Float | VYST. – LIM. – L. 2 – VY.L.2 | Hysteresis | -1999..9999
0x10 | *0x00A0 | 0x000204EEMMMMMM | 40160 | Float | VYST. – LIM. – L. 2 – PE.L.2 | Hysteresis | 0,001..9999
0x10 | 0x00A8 | 0x000204EEMMMMMM | 40168 | Float | VYST. – LIM. – L. 2 – C. L.2 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x06 | 0x00AA | 0x0200XX | 40170 | List | VYST. – LIM. – L. 3 – VS.L.3 | Input value for limit 3 | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x00AC | 0x0200XX | 40172 | List | VYST. – LIM. – L. 3 – MO.L.3 | Mode of controling limit | 0=HYST., 1=FR.TO, 2=DOSE
0x06 | 0x00AE | 0x0200XX | 40174 | List | VYST. – LIM. – L. 3 – TY.L.3 | Limit type | 0=CLOS., 1=OPEN
0x10 | 0x00B0 | 0x000204EEMMMMMM | 40176 | Float | VYST. – LIM. – L. 3 – M. L.3 | Limit value | -1999..9999
0x10 | 0x00B2 | 0x000204EEMMMMMM | 40178 | Float | VYST. – LIM. – L. 3 – H. L.3 | Hysteresis | 0..9999
0x10 | *0x00B0 | 0x000204EEMMMMMM | 40176 | Float | VYST. – LIM. – L. 3 – ZA.L.3 | Limit value | -1999..9999
0x10 | *0x00B2 | 0x000204EEMMMMMM | 40178 | Float | VYST. – LIM. – L. 3 – VY.L.3 | Hysteresis | -1999..9999
0x10 | *0x00B2 | 0x000204EEMMMMMM | 40178 | Float | VYST. – LIM. – L. 3 – PE.L.3 | Hysteresis | 0,001..9999
0x10 | 0x00BA | 0x000204EEMMMMMM | 40186 | Float | VYST. – LIM. – L. 3 – C. L.3 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x06 | 0x00BC | 0x0200XX | 40188 | List | VYST. – LIM. – L. 4 – VS.L.4 | Input value for limit 4 | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x00BE | 0x0200XX | 40190 | List | VYST. – LIM. – L. 4 – MO.L.4 | Mode of controling limit | 0=HYST., 1=FR.TO, 2=DOSE
0x06 | 0x00C0 | 0x0200XX | 40192 | List | VYST. – LIM. – L. 4 – TY.L.4 | Limit type | 0=CLOS., 1=OPEN
0x10 | 0x00C2 | 0x000204EEMMMMMM | 40194 | Float | VYST. – LIM. – L. 4 – M. L.4 | Limit value | -1999..9999
0x10 | 0x00C4 | 0x000204EEMMMMMM | 40196 | Float | VYST. – LIM. – L. 4 – H. L.4 | Hysteresis | 0..9999
0x10 | *0x00C2 | 0x000204EEMMMMMM | 40194 | Float | VYST. – LIM. – L. 4 – ZA.L.4 | Limit value | -1999..9999
0x10 | *0x00C4 | 0x000204EEMMMMMM | 40196 | Float | VYST. – LIM. – L. 4 – VY.L.4 | Hysteresis | -1999..9999
0x10 | *0x00C4 | 0x000204EEMMMMMM | 40196 | Float | VYST. – LIM. – L. 4 – PE.L.4 | Hysteresis | 0,001..9999
0x10 | 0x00CC | 0x000204EEMMMMMM | 40204 | Float | VYST. – LIM. – L. 4 – C. L.4 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x06 | 0x00CE | 0x0200XX | 40206 | List | VYST. – DATA – BAUD | Transfer rate | 0= 0.6, 1= 1.2, 2= 2.4, 3= 4.8, 4= 9.6, 5= 19.2, 6= 38.4, 7= 57.6, 8=115.2, 9=230.4
0x10 | 0x00D0 | 0x000204EEMMMMMM | 40208 | Float | VYST. – DATA – ADR. | Instrument address | 0..31
0x06 | 0x00D6 | 0x0200XX | 40214 | List | VYST. – DATA – PROT. | Communication protocol | 0=ASCI., 1=M.BUS, 2=MODB.
0x06 | 0x00D8 | 0x0200XX | 40216 | List | VYST. – ANAL. – VS.A.V. | Input value for analog output | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x00DA | 0x0200XX | 40218 | List | VYST. – ANAL. – TY.A.V. | Type | 0=0-20, 1=Er4T, 2=4-2T, 3=Er 4, 4=4-20, 5=i0-5, 6=u0-2, 7=u0-5, 8=0-10, 9=+-10
0x10 | 0x00DC | 0x000204EEMMMMMM | 40220 | Float | VYST. – ANAL. – MI.A.V. | Minimum display value corresponding with bottom value of selected A.O. range | -1999..9999
0x10 | 0x00DE | 0x000204EEMMMMMM | 40222 | Float | VYST. – ANAL. – MA.A.V. | Maximum display value corresponding with top value of selected A.O. range | -1999..9999
0x06 | 0x00E0 | 0x0200XX | 40224 | List | VYST. – DISP. – TRV. | Value to be permanent displayed | 0=NO, 1=CH. A, 2=FIL.A, 3=M. FN., 4=MIN., 5=MAX., 6=L. 1, 7=L. 2, 8=L. 3, 9=L. 4, 10=TIME, 11=DATE, 12=TARE, 13=P.TAR., 14=C. J.
0x06 | 0x00E2 | 0x0200XX | 40226 | List | VYST. – DISP. – BAR.0 | Color of value display | 0=RED, 1=GRN., 2=ORAN.
0x10 | 0x00E4 | 0x000204EEMMMMMM | 40228 | Float | VYST. – DISP. – D.L. 1. | Value of color 0 / 1 | -1999..9999
0x06 | 0x00E6 | 0x0200XX | 40230 | List | VYST. – DISP. – BAR.1 | Color of value display when relay 1 is on | 0=RED, 1=GRN., 2=ORAN.
0x10 | 0x00E8 | 0x000204EEMMMMMM | 40232 | Float | VYST. – DISP. – D.L. 2. | Value of color 1 / 2 | -1999..9999
0x06 | 0x00EA | 0x0200XX | 40234 | List | VYST. – DISP. – BAR.2 | Display and main bargraph color when second relay is ON. First relay is not sigificant. | 0=RED, 1=GRN., 2=ORAN.
0x06 | 0x00EC | 0x0200XX | 40236 | List | VYST. – DISP. – JAS | Brightness of displey | 0= 0%, 1= 25%, 2= 50%, 3= 75%, 4=100%
0x06 | 0x00FA | 0x0200XX | 40250 | List | SERV. – JAZ. | Language variation of menu | 0=CZE., 1=ENGL.