## Modbus
Stav rele / State of relays
0x01 | 0x0000 | 0x0008
Externi vstupy / External inputs
0x02 | 0x0000 | 0x0008
Identifikace / Indentification
0x11
Výkonné příkazy / Do action
0x05 | 0x0000 | 0xFF00 | 0 |  |  | Clear memory of measured datas
Vyčtení naměřených a vypočtených hodnot / Reading of measured or evaluated values
0x04 | 0x0004 | 0x0002 | 30004 | float | FIL. A
0x04 | 0x0006 | 0x0002 | 30006 | float | MAT. FN.
Vyčtení hodnot z menu / Reading menu item values
0x03 | 0x0004 | 0x0001 | 40004 | List | INPUTS – CONFIG. – MODE | Instrument mode | 0=MANUAL, 1=SINE, 2=RAMP, 3=TRIANG., 4=SQUARE, 5=RANDOM
0x03 | 0x0006 | 0x0002 | 40006 | Float | INPUTS – CONFIG. – MIN | Value corresponding w/ minimum value of input range | -99999..999999
0x03 | 0x0008 | 0x0002 | 40008 | Float | INPUTS – CONFIG. – VALUE | Actual value which was setted by hand | -99999..999999
0x03 | 0x000A | 0x0002 | 40010 | Float | INPUTS – CONFIG. – MAX | Value corresponding w/ maximum value of input range | -99999..999999
0x03 | 0x000C | 0x0002 | 40012 | Float | INPUTS – CONFIG. – STEP 1 | Change size when key UP or DOWN are pressed | 0..999999
0x03 | 0x000E | 0x0002 | 40014 | Float | INPUTS – CONFIG. – STEP 2 | Change size when key LEFT + UP or DOWN are pressed | 0..999999
0x03 | 0x0010 | 0x0002 | 40016 | Float | INPUTS – CONFIG. – FREQ. | Automatic generated signal frequency | 0,00024..3
0x03 | 0x0012 | 0x0002 | 40018 | Float | INPUTS – CONFIG. – MIN. T. | Minimal length of one segment of randomly generated signal | 0,2..4166
0x03 | 0x0014 | 0x0002 | 40020 | Float | INPUTS – CONFIG. – MAX. T. | Maximal length of one segment of randomly generated signal | 0,2..4166
0x03 | 0x0016 | 0x0002 | 40022 | Float | INPUTS – CONFIG. – COUNT | Number of periodes of automatickly generated signal. If it is set to 0 (zero) signal is generated continually. | 0..65535
0x03 | 0x0018 | 0x0001 | 40024 | List | INPUTS – CONFIG. – BACKUP | Handly setted value will be stored to EEPROM. | 0=NO, 1=YES
0x03 | 0x001E | 0x0001 | 40030 | List | INPUTS – EXT. IN. – EXT. 1 | Setting auxiliary input 1 | 0=OFF, 1=HOLD, 2=LOCK. K., 3=B. PASS, 4=SAVE, 5=K1 UP, 6=K1 DWN., 7=K2 UP, 8=K2 DWN., 9=MIN. V., 10=MAX. V., 11=UP, 12=DOWN, 13=START, 14=STOP, 15=ST.-ST., 16=ST. 1/2
0x03 | 0x0020 | 0x0001 | 40032 | List | INPUTS – EXT. IN. – EXT. 2 | Setting auxiliary input 2 | 0=OFF, 1=HOLD, 2=LOCK. K., 3=B. PASS, 4=SAVE, 5=K1 UP, 6=K1 DWN., 7=K2 UP, 8=K2 DWN., 9=MIN. V., 10=MAX. V., 11=UP, 12=DOWN, 13=START, 14=STOP, 15=ST.-ST., 16=ST. 1/2
0x03 | 0x0022 | 0x0001 | 40034 | List | INPUTS – EXT. IN. – EXT. 3 | Setting auxiliary input 3 | 0=OFF, 1=HOLD, 2=LOCK. K., 3=B. PASS, 4=SAVE, 5=K1 UP, 6=K1 DWN., 7=K2 UP, 8=K2 DWN., 9=MIN. V., 10=MAX. V., 11=UP, 12=DOWN, 13=START, 14=STOP, 15=ST.-ST., 16=ST. 1/2
0x03 | 0x0024 | 0x0002 | 40036 | Float | INPUTS – EXT. IN. – STEP | Value increasing/decreasing step per 10 ms. | 0..999999
0x03 | 0x0026 | 0x0001 | 40038 | List | INPUTS – EXT. IN. – M. HOLD | Range of instrument blocation | 0=DISPL., 1=DIS.+A.O., 2=D.+A.O.+L., 3=ALL
0x03 | 0x0028 | 0x0001 | 40040 | List | INPUTS – KEYS – LEFT – FN. LE. | Function setting for key LEFT | 0=NO, 1=MENU, 2=MANUAL, 3=START, 4=STOP, 5=ST.-ST., 6=602 A.O.
0x03 | 0x002A | 0x0001 | 40042 | List | INPUTS – KEYS – LEFT – MNU. LE. | Choice of menu item | 0=TYP. A.O., 1=AUT. A.O., 2=VALUE, 3=STEP 1, 4=STEP 2, 5=FREQ., 6=COUNT
0x03 | 0x002C | 0x0001 | 40044 | List | INPUTS – KEYS – DOWN – FN. DO. | Function setting for key DOWN | 0=NO, 1=MENU, 2=MANUAL, 3=START, 4=STOP, 5=ST.-ST., 6=602 A.O.
0x03 | 0x002E | 0x0001 | 40046 | List | INPUTS – KEYS – DOWN – MNU. DO. | Choice of menu item | 0=TYP. A.O., 1=AUT. A.O., 2=VALUE, 3=STEP 1, 4=STEP 2, 5=FREQ., 6=COUNT
0x03 | 0x0030 | 0x0001 | 40048 | List | INPUTS – KEYS – UP – FN. UP | Function setting for key UP | 0=NO, 1=MENU, 2=MANUAL, 3=START, 4=STOP, 5=ST.-ST., 6=602 A.O.
0x03 | 0x0032 | 0x0001 | 40050 | List | INPUTS – KEYS – UP – MNU. UP | Choice of menu item | 0=TYP. A.O., 1=AUT. A.O., 2=VALUE, 3=STEP 1, 4=STEP 2, 5=FREQ., 6=COUNT
0x03 | 0x0034 | 0x0001 | 40052 | List | INPUTS – KEYS – ENTER – FN. EN. | Function setting for key ENTER | 0=NO, 1=MENU, 2=MANUAL, 3=START, 4=STOP, 5=ST.-ST., 6=602 A.O.
0x03 | 0x0036 | 0x0001 | 40054 | List | INPUTS – KEYS – ENTER – MNU. EN. | Choice of menu item | 0=TYP. A.O., 1=AUT. A.O., 2=VALUE, 3=STEP 1, 4=STEP 2, 5=FREQ., 6=COUNT
0x03 | 0x0038 | 0x0001 | 40056 | List | CHANNE. – CHAN. A – FILTER – MOD. F.A | Filter mode | 0=NO, 1=ROUND
0x03 | 0x003A | 0x0002 | 40058 | Float | CHANNE. – CHAN. A – FILTER – CON. F.A | Filter constant | 0,00001..999999
0x03 | 0x003C | 0x0001 | 40060 | List | CHANNE. – CHAN. A – FORM. A | Projection format | 0=000000., 1=00000.o, 2=0000.oo, 3=000.ooo, 4=00.oooo, 5=0.ooooo, 6=FLOA. P.
0x03 | 0x003E | 0x0001 | 40062 | Desc | CHANNE. – CHAN. A – DESC. A | Description setting (measured quantity unit) | Char(32)..Char(127)
0x03 | 0x0046 | 0x0001 | 40070 | List | CHANNE. – MAT. FN. – MATH. F. | Mathematic function select | 0=OFF, 1=MULTIN., 2=1/MUL., 3=LOGAR., 4=EXPON., 5=POWER, 6=ROOT, 7=SIN X
0x03 | 0x0048 | 0x0002 | 40072 | Float | CHANNE. – MAT. FN. – CON. A | Constant A | -99999..999999
0x03 | 0x004A | 0x0002 | 40074 | Float | CHANNE. – MAT. FN. – CON. B | Constant B | -99999..999999
0x03 | 0x004C | 0x0002 | 40076 | Float | CHANNE. – MAT. FN. – CON. C | Constant C | -99999..999999
0x03 | 0x004E | 0x0002 | 40078 | Float | CHANNE. – MAT. FN. – CON. D | Constant D | -99999..999999
0x03 | 0x0050 | 0x0002 | 40080 | Float | CHANNE. – MAT. FN. – CON. E | Constant E | -99999..999999
0x03 | 0x0052 | 0x0002 | 40082 | Float | CHANNE. – MAT. FN. – CON. F | Constant F | -99999..999999
0x03 | 0x0054 | 0x0001 | 40084 | List | CHANNE. – MAT. FN. – FORM. M | Projection format | 0=000000., 1=00000.o, 2=0000.oo, 3=000.ooo, 4=00.oooo, 5=0.ooooo, 6=FLOA. P.
0x03 | 0x0056 | 0x0001 | 40086 | Desc | CHANNE. – MAT. FN. – DESC. M | Description setting (measured quantity unit) | Char(32)..Char(127)
0x03 | 0x0066 | 0x0001 | 40102 | List | OUTPUT. – LIMITS – LIM 1 – INP. L.1 | Input value for limit 1 | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x03 | 0x0068 | 0x0001 | 40104 | List | OUTPUT. – LIMITS – LIM 1 – MOD. L.1 | Mode of controling limit | 0=HYSTER., 1=FROM. . ., 2=DOSING
0x03 | 0x006A | 0x0001 | 40106 | List | OUTPUT. – LIMITS – LIM 1 – TYP. L.1 | Limit type | 0=CLOSE, 1=OPEN
0x03 | 0x006C | 0x0002 | 40108 | Float | OUTPUT. – LIMITS – LIM 1 – LIM. L.1 | Limit value | -99999..999999
0x03 | 0x006E | 0x0002 | 40110 | Float | OUTPUT. – LIMITS – LIM 1 – HYS. L.1 | Hysteresis | 0..999999
0x03 | *0x006C | 0x0002 | 40108 | Float | OUTPUT. – LIMITS – LIM 1 – ON L.1 | Limit value | -99999..999999
0x03 | *0x006E | 0x0002 | 40110 | Float | OUTPUT. – LIMITS – LIM 1 – OFF L.1 | Hysteresis | -99999..999999
0x03 | *0x006E | 0x0002 | 40110 | Float | OUTPUT. – LIMITS – LIM 1 – PER. L.1 | Hysteresis | 0,00001..999999
0x03 | 0x0076 | 0x0002 | 40118 | Float | OUTPUT. – LIMITS – LIM 1 – TIM. L.1 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x03 | 0x0078 | 0x0001 | 40120 | List | OUTPUT. – LIMITS – LIM 2 – INP. L.2 | Input value for limit 2 | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x03 | 0x007A | 0x0001 | 40122 | List | OUTPUT. – LIMITS – LIM 2 – MOD. L.2 | Mode of controling limit | 0=HYSTER., 1=FROM. . ., 2=DOSING
0x03 | 0x007C | 0x0001 | 40124 | List | OUTPUT. – LIMITS – LIM 2 – TYP. L.2 | Limit type | 0=CLOSE, 1=OPEN
0x03 | 0x007E | 0x0002 | 40126 | Float | OUTPUT. – LIMITS – LIM 2 – LIM. L.2 | Limit value | -99999..999999
0x03 | 0x0080 | 0x0002 | 40128 | Float | OUTPUT. – LIMITS – LIM 2 – HYS. L.2 | Hysteresis | 0..999999
0x03 | *0x007E | 0x0002 | 40126 | Float | OUTPUT. – LIMITS – LIM 2 – ON L.2 | Limit value | -99999..999999
0x03 | *0x0080 | 0x0002 | 40128 | Float | OUTPUT. – LIMITS – LIM 2 – OFF L.2 | Hysteresis | -99999..999999
0x03 | *0x0080 | 0x0002 | 40128 | Float | OUTPUT. – LIMITS – LIM 2 – PER. L.2 | Hysteresis | 0,00001..999999
0x03 | 0x0088 | 0x0002 | 40136 | Float | OUTPUT. – LIMITS – LIM 2 – TIM. L.2 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x03 | 0x008A | 0x0001 | 40138 | List | OUTPUT. – LIMITS – LIM 3 – INP. L.3 | Input value for limit 3 | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x03 | 0x008C | 0x0001 | 40140 | List | OUTPUT. – LIMITS – LIM 3 – MOD. L.3 | Mode of controling limit | 0=HYSTER., 1=FROM. . ., 2=DOSING
0x03 | 0x008E | 0x0001 | 40142 | List | OUTPUT. – LIMITS – LIM 3 – TYP. L.3 | Limit type | 0=CLOSE, 1=OPEN
0x03 | 0x0090 | 0x0002 | 40144 | Float | OUTPUT. – LIMITS – LIM 3 – LIM. L.3 | Limit value | -99999..999999
0x03 | 0x0092 | 0x0002 | 40146 | Float | OUTPUT. – LIMITS – LIM 3 – HYS. L.3 | Hysteresis | 0..999999
0x03 | *0x0090 | 0x0002 | 40144 | Float | OUTPUT. – LIMITS – LIM 3 – ON L.3 | Limit value | -99999..999999
0x03 | *0x0092 | 0x0002 | 40146 | Float | OUTPUT. – LIMITS – LIM 3 – OFF L.3 | Hysteresis | -99999..999999
0x03 | *0x0092 | 0x0002 | 40146 | Float | OUTPUT. – LIMITS – LIM 3 – PER. L.3 | Hysteresis | 0,00001..999999
0x03 | 0x009A | 0x0002 | 40154 | Float | OUTPUT. – LIMITS – LIM 3 – TIM. L.3 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x03 | 0x009C | 0x0001 | 40156 | List | OUTPUT. – LIMITS – LIM 4 – INP. L.4 | Input value for limit 4 | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x03 | 0x009E | 0x0001 | 40158 | List | OUTPUT. – LIMITS – LIM 4 – MOD. L.4 | Mode of controling limit | 0=HYSTER., 1=FROM. . ., 2=DOSING
0x03 | 0x00A0 | 0x0001 | 40160 | List | OUTPUT. – LIMITS – LIM 4 – TYP. L.4 | Limit type | 0=CLOSE, 1=OPEN
0x03 | 0x00A2 | 0x0002 | 40162 | Float | OUTPUT. – LIMITS – LIM 4 – LIM. L.4 | Limit value | -99999..999999
0x03 | 0x00A4 | 0x0002 | 40164 | Float | OUTPUT. – LIMITS – LIM 4 – HYS. L.4 | Hysteresis | 0..999999
0x03 | *0x00A2 | 0x0002 | 40162 | Float | OUTPUT. – LIMITS – LIM 4 – ON L.4 | Limit value | -99999..999999
0x03 | *0x00A4 | 0x0002 | 40164 | Float | OUTPUT. – LIMITS – LIM 4 – OFF L.4 | Hysteresis | -99999..999999
0x03 | *0x00A4 | 0x0002 | 40164 | Float | OUTPUT. – LIMITS – LIM 4 – PER. L.4 | Hysteresis | 0,00001..999999
0x03 | 0x00AC | 0x0002 | 40172 | Float | OUTPUT. – LIMITS – LIM 4 – TIM. L.4 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x03 | 0x00AE | 0x0001 | 40174 | List | OUTPUT. – DATA – BAUD | Transfer rate | 0= 600, 1= 1200, 2= 2400, 3= 4800, 4= 9600, 5= 19200, 6= 38400, 7= 57600, 8=115200, 9=230400
0x03 | 0x00B0 | 0x0002 | 40176 | Float | OUTPUT. – DATA – ADDR. | Instrument address | 0..31
0x03 | 0x00B6 | 0x0001 | 40182 | List | OUTPUT. – DATA – PROT. | Communication protocol | 0=ASCII, 1=M. BUS, 2=MODBUS
0x03 | 0x00B8 | 0x0001 | 40184 | List | OUTPUT. – AN. OUT. – INP. A.O. | Input value for analog output | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x03 | 0x00BA | 0x0001 | 40186 | List | OUTPUT. – AN. OUT. – TYP. A.O. | Type | 0=0-20mA, 1=Er4- T, 2=4-20 T, 3=Er4-20, 4=4-20mA, 5=0- 5mA, 6=0- 2 V, 7=0- 5 V, 8=0-10 V, 9=+-10 V
0x03 | 0x00BE | 0x0002 | 40190 | Float | OUTPUT. – AN. OUT. – MIN A.O. | Minimum display value corresponding with bottom value of selected A.O. range | -99999..999999
0x03 | 0x00C0 | 0x0002 | 40192 | Float | OUTPUT. – AN. OUT. – MAX A.O. | Maximum display value corresponding with top value of selected A.O. range | -99999..999999
0x03 | 0x00C2 | 0x0001 | 40194 | List | OUTPUT. – DISP. – PERM. | Value to be permanent displayed | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x03 | 0x00C4 | 0x0001 | 40196 | List | OUTPUT. – DISP. – BRIGHT | Brightness of displey | 0= 0%, 1= 25%, 2= 50%, 3= 75%, 4= 100%
0x03 | 0x00CC | 0x0001 | 40204 | List | SERVIC. – LANG. | Language variation of menu | 0=CZECH, 1=ENGL.
Nastavení hodnot menu / Setting menu item values
0x06 | 0x0004 | 0x00XX | 40004 | List | INPUTS – CONFIG. – MODE | Instrument mode | 0=MANUAL, 1=SINE, 2=RAMP, 3=TRIANG., 4=SQUARE, 5=RANDOM
0x10 | 0x0006 | 0x000204EEMMMMMM | 40006 | Float | INPUTS – CONFIG. – MIN | Scale | -99999..999999
0x10 | 0x0008 | 0x000204EEMMMMMM | 40008 | Float | INPUTS – CONFIG. – VALUE | Actual value which was setted by hand | -99999..999999
0x10 | 0x000A | 0x000204EEMMMMMM | 40010 | Float | INPUTS – CONFIG. – MAX | Value corresponding w/ maximum value of input range | -99999..999999
0x10 | 0x000C | 0x000204EEMMMMMM | 40012 | Float | INPUTS – CONFIG. – STEP 1 | Change size when key UP or DOWN are pressed | 0..999999
0x10 | 0x000E | 0x000204EEMMMMMM | 40014 | Float | INPUTS – CONFIG. – STEP 2 | Change size when key LEFT + UP or DOWN are pressed | 0..999999
0x10 | 0x0010 | 0x000204EEMMMMMM | 40016 | Float | INPUTS – CONFIG. – FREQ. | Automatic generated signal frequency | 0,00024..3
0x10 | 0x0012 | 0x000204EEMMMMMM | 40018 | Float | INPUTS – CONFIG. – MIN. T. | Minimal length of one segment of randomly generated signal | 0,2..4166
0x10 | 0x0014 | 0x000204EEMMMMMM | 40020 | Float | INPUTS – CONFIG. – MAX. T. | Maximal length of one segment of randomly generated signal | 0,2..4166
0x10 | 0x0016 | 0x000204EEMMMMMM | 40022 | Float | INPUTS – CONFIG. – COUNT | Number of periodes of automatickly generated signal. If it is set to 0 (zero) signal is generated continually. | 0..65535
0x06 | 0x0018 | 0x00XX | 40024 | List | INPUTS – CONFIG. – BACKUP | Handly setted value will be stored to EEPROM. | 0=NO, 1=YES
0x06 | 0x001E | 0x00XX | 40030 | List | INPUTS – EXT. IN. – EXT. 1 | Setting auxiliary input 1 | 0=OFF, 1=HOLD, 2=LOCK. K., 3=B. PASS, 4=SAVE, 5=K1 UP, 6=K1 DWN., 7=K2 UP, 8=K2 DWN., 9=MIN. V., 10=MAX. V., 11=UP, 12=DOWN, 13=START, 14=STOP, 15=ST.-ST., 16=ST. 1/2
0x06 | 0x0020 | 0x00XX | 40032 | List | INPUTS – EXT. IN. – EXT. 2 | Setting auxiliary input 2 | 0=OFF, 1=HOLD, 2=LOCK. K., 3=B. PASS, 4=SAVE, 5=K1 UP, 6=K1 DWN., 7=K2 UP, 8=K2 DWN., 9=MIN. V., 10=MAX. V., 11=UP, 12=DOWN, 13=START, 14=STOP, 15=ST.-ST., 16=ST. 1/2
0x06 | 0x0022 | 0x00XX | 40034 | List | INPUTS – EXT. IN. – EXT. 3 | Setting auxiliary input 3 | 0=OFF, 1=HOLD, 2=LOCK. K., 3=B. PASS, 4=SAVE, 5=K1 UP, 6=K1 DWN., 7=K2 UP, 8=K2 DWN., 9=MIN. V., 10=MAX. V., 11=UP, 12=DOWN, 13=START, 14=STOP, 15=ST.-ST., 16=ST. 1/2
0x10 | 0x0024 | 0x000204EEMMMMMM | 40036 | Float | INPUTS – EXT. IN. – STEP | Value increasing/decreasing step per 10 ms. | 0..999999
0x06 | 0x0026 | 0x00XX | 40038 | List | INPUTS – EXT. IN. – M. HOLD | Range of instrument blocation | 0=DISPL., 1=DIS.+A.O., 2=D.+A.O.+L., 3=ALL
0x06 | 0x0028 | 0x00XX | 40040 | List | INPUTS – KEYS – LEFT – FN. LE. | Function setting for key LEFT | 0=NO, 1=MENU, 2=MANUAL, 3=START, 4=STOP, 5=ST.-ST., 6=602 A.O.
0x06 | 0x002A | 0x00XX | 40042 | List | INPUTS – KEYS – LEFT – MNU. LE. | Choice of menu item | 0=TYP. A.O., 1=AUT. A.O., 2=VALUE, 3=STEP 1, 4=STEP 2, 5=FREQ., 6=COUNT
0x06 | 0x002C | 0x00XX | 40044 | List | INPUTS – KEYS – DOWN – FN. DO. | Function setting for key DOWN | 0=NO, 1=MENU, 2=MANUAL, 3=START, 4=STOP, 5=ST.-ST., 6=602 A.O.
0x06 | 0x002E | 0x00XX | 40046 | List | INPUTS – KEYS – DOWN – MNU. DO. | Choice of menu item | 0=TYP. A.O., 1=AUT. A.O., 2=VALUE, 3=STEP 1, 4=STEP 2, 5=FREQ., 6=COUNT
0x06 | 0x0030 | 0x00XX | 40048 | List | INPUTS – KEYS – UP – FN. UP | Function setting for key UP | 0=NO, 1=MENU, 2=MANUAL, 3=START, 4=STOP, 5=ST.-ST., 6=602 A.O.
0x06 | 0x0032 | 0x00XX | 40050 | List | INPUTS – KEYS – UP – MNU. UP | Choice of menu item | 0=TYP. A.O., 1=AUT. A.O., 2=VALUE, 3=STEP 1, 4=STEP 2, 5=FREQ., 6=COUNT
0x06 | 0x0034 | 0x00XX | 40052 | List | INPUTS – KEYS – ENTER – FN. EN. | Function setting for key ENTER | 0=NO, 1=MENU, 2=MANUAL, 3=START, 4=STOP, 5=ST.-ST., 6=602 A.O.
0x06 | 0x0036 | 0x00XX | 40054 | List | INPUTS – KEYS – ENTER – MNU. EN. | Choice of menu item | 0=TYP. A.O., 1=AUT. A.O., 2=VALUE, 3=STEP 1, 4=STEP 2, 5=FREQ., 6=COUNT
0x06 | 0x0038 | 0x00XX | 40056 | List | CHANNE. – CHAN. A – FILTER – MOD. F.A | Filter mode | 0=NO, 1=ROUND
0x10 | 0x003A | 0x000204EEMMMMMM | 40058 | Float | CHANNE. – CHAN. A – FILTER – CON. F.A | Filter constant | 0,00001..999999
0x06 | 0x003C | 0x00XX | 40060 | List | CHANNE. – CHAN. A – FORM. A | Projection format | 0=000000., 1=00000.o, 2=0000.oo, 3=000.ooo, 4=00.oooo, 5=0.ooooo, 6=FLOA. P.
0x06 | 0x003E | 0xXXXX | 40062 | Desc | CHANNE. – CHAN. A – DESC. A | Description setting (Measured quantity unit) - 3 ASCII characters | Char(32)..Char(127)
0x06 | 0x0046 | 0x00XX | 40070 | List | CHANNE. – MAT. FN. – MATH. F. | Mathematic function select | 0=OFF, 1=MULTIN., 2=1/MUL., 3=LOGAR., 4=EXPON., 5=POWER, 6=ROOT, 7=SIN X
0x10 | 0x0048 | 0x000204EEMMMMMM | 40072 | Float | CHANNE. – MAT. FN. – CON. A | Constant A | -99999..999999
0x10 | 0x004A | 0x000204EEMMMMMM | 40074 | Float | CHANNE. – MAT. FN. – CON. B | Constant B | -99999..999999
0x10 | 0x004C | 0x000204EEMMMMMM | 40076 | Float | CHANNE. – MAT. FN. – CON. C | Constant C | -99999..999999
0x10 | 0x004E | 0x000204EEMMMMMM | 40078 | Float | CHANNE. – MAT. FN. – CON. D | Constant D | -99999..999999
0x10 | 0x0050 | 0x000204EEMMMMMM | 40080 | Float | CHANNE. – MAT. FN. – CON. E | Constant E | -99999..999999
0x10 | 0x0052 | 0x000204EEMMMMMM | 40082 | Float | CHANNE. – MAT. FN. – CON. F | Constant F | -99999..999999
0x06 | 0x0054 | 0x00XX | 40084 | List | CHANNE. – MAT. FN. – FORM. M | Projection format | 0=000000., 1=00000.o, 2=0000.oo, 3=000.ooo, 4=00.oooo, 5=0.ooooo, 6=FLOA. P.
0x06 | 0x0056 | 0xXXXX | 40086 | Desc | CHANNE. – MAT. FN. – DESC. M | Description setting (Measured quantity unit) - 3 ASCII characters | Char(32)..Char(127)
0x06 | 0x0066 | 0x00XX | 40102 | List | OUTPUT. – LIMITS – LIM 1 – INP. L.1 | Input value for limit 1 | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x06 | 0x0068 | 0x00XX | 40104 | List | OUTPUT. – LIMITS – LIM 1 – MOD. L.1 | Mode of controling limit | 0=HYSTER., 1=FROM. . ., 2=DOSING
0x06 | 0x006A | 0x00XX | 40106 | List | OUTPUT. – LIMITS – LIM 1 – TYP. L.1 | Limit type | 0=CLOSE, 1=OPEN
0x10 | 0x006C | 0x000204EEMMMMMM | 40108 | Float | OUTPUT. – LIMITS – LIM 1 – LIM. L.1 | Limit value | -99999..999999
0x10 | 0x006E | 0x000204EEMMMMMM | 40110 | Float | OUTPUT. – LIMITS – LIM 1 – HYS. L.1 | Hysteresis | 0..999999
0x10 | *0x006C | 0x000204EEMMMMMM | 40108 | Float | OUTPUT. – LIMITS – LIM 1 – ON L.1 | Limit value | -99999..999999
0x10 | *0x006E | 0x000204EEMMMMMM | 40110 | Float | OUTPUT. – LIMITS – LIM 1 – OFF L.1 | Hysteresis | -99999..999999
0x10 | *0x006E | 0x000204EEMMMMMM | 40110 | Float | OUTPUT. – LIMITS – LIM 1 – PER. L.1 | Hysteresis | 0,00001..999999
0x10 | 0x0076 | 0x000204EEMMMMMM | 40118 | Float | OUTPUT. – LIMITS – LIM 1 – TIM. L.1 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x06 | 0x0078 | 0x00XX | 40120 | List | OUTPUT. – LIMITS – LIM 2 – INP. L.2 | Input value for limit 2 | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x06 | 0x007A | 0x00XX | 40122 | List | OUTPUT. – LIMITS – LIM 2 – MOD. L.2 | Mode of controling limit | 0=HYSTER., 1=FROM. . ., 2=DOSING
0x06 | 0x007C | 0x00XX | 40124 | List | OUTPUT. – LIMITS – LIM 2 – TYP. L.2 | Limit type | 0=CLOSE, 1=OPEN
0x10 | 0x007E | 0x000204EEMMMMMM | 40126 | Float | OUTPUT. – LIMITS – LIM 2 – LIM. L.2 | Limit value | -99999..999999
0x10 | 0x0080 | 0x000204EEMMMMMM | 40128 | Float | OUTPUT. – LIMITS – LIM 2 – HYS. L.2 | Hysteresis | 0..999999
0x10 | *0x007E | 0x000204EEMMMMMM | 40126 | Float | OUTPUT. – LIMITS – LIM 2 – ON L.2 | Limit value | -99999..999999
0x10 | *0x0080 | 0x000204EEMMMMMM | 40128 | Float | OUTPUT. – LIMITS – LIM 2 – OFF L.2 | Hysteresis | -99999..999999
0x10 | *0x0080 | 0x000204EEMMMMMM | 40128 | Float | OUTPUT. – LIMITS – LIM 2 – PER. L.2 | Hysteresis | 0,00001..999999
0x10 | 0x0088 | 0x000204EEMMMMMM | 40136 | Float | OUTPUT. – LIMITS – LIM 2 – TIM. L.2 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x06 | 0x008A | 0x00XX | 40138 | List | OUTPUT. – LIMITS – LIM 3 – INP. L.3 | Input value for limit 3 | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x06 | 0x008C | 0x00XX | 40140 | List | OUTPUT. – LIMITS – LIM 3 – MOD. L.3 | Mode of controling limit | 0=HYSTER., 1=FROM. . ., 2=DOSING
0x06 | 0x008E | 0x00XX | 40142 | List | OUTPUT. – LIMITS – LIM 3 – TYP. L.3 | Limit type | 0=CLOSE, 1=OPEN
0x10 | 0x0090 | 0x000204EEMMMMMM | 40144 | Float | OUTPUT. – LIMITS – LIM 3 – LIM. L.3 | Limit value | -99999..999999
0x10 | 0x0092 | 0x000204EEMMMMMM | 40146 | Float | OUTPUT. – LIMITS – LIM 3 – HYS. L.3 | Hysteresis | 0..999999
0x10 | *0x0090 | 0x000204EEMMMMMM | 40144 | Float | OUTPUT. – LIMITS – LIM 3 – ON L.3 | Limit value | -99999..999999
0x10 | *0x0092 | 0x000204EEMMMMMM | 40146 | Float | OUTPUT. – LIMITS – LIM 3 – OFF L.3 | Hysteresis | -99999..999999
0x10 | *0x0092 | 0x000204EEMMMMMM | 40146 | Float | OUTPUT. – LIMITS – LIM 3 – PER. L.3 | Hysteresis | 0,00001..999999
0x10 | 0x009A | 0x000204EEMMMMMM | 40154 | Float | OUTPUT. – LIMITS – LIM 3 – TIM. L.3 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x06 | 0x009C | 0x00XX | 40156 | List | OUTPUT. – LIMITS – LIM 4 – INP. L.4 | Input value for limit 4 | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x06 | 0x009E | 0x00XX | 40158 | List | OUTPUT. – LIMITS – LIM 4 – MOD. L.4 | Mode of controling limit | 0=HYSTER., 1=FROM. . ., 2=DOSING
0x06 | 0x00A0 | 0x00XX | 40160 | List | OUTPUT. – LIMITS – LIM 4 – TYP. L.4 | Limit type | 0=CLOSE, 1=OPEN
0x10 | 0x00A2 | 0x000204EEMMMMMM | 40162 | Float | OUTPUT. – LIMITS – LIM 4 – LIM. L.4 | Limit value | -99999..999999
0x10 | 0x00A4 | 0x000204EEMMMMMM | 40164 | Float | OUTPUT. – LIMITS – LIM 4 – HYS. L.4 | Hysteresis | 0..999999
0x10 | *0x00A2 | 0x000204EEMMMMMM | 40162 | Float | OUTPUT. – LIMITS – LIM 4 – ON L.4 | Limit value | -99999..999999
0x10 | *0x00A4 | 0x000204EEMMMMMM | 40164 | Float | OUTPUT. – LIMITS – LIM 4 – OFF L.4 | Hysteresis | -99999..999999
0x10 | *0x00A4 | 0x000204EEMMMMMM | 40164 | Float | OUTPUT. – LIMITS – LIM 4 – PER. L.4 | Hysteresis | 0,00001..999999
0x10 | 0x00AC | 0x000204EEMMMMMM | 40172 | Float | OUTPUT. – LIMITS – LIM 4 – TIM. L.4 | Time of delay between meeting the condition and the relay switchon/switchoff (according to type of switching) | -99,9..99,9
0x06 | 0x00AE | 0x00XX | 40174 | List | OUTPUT. – DATA – BAUD | Transfer rate | 0= 600, 1= 1200, 2= 2400, 3= 4800, 4= 9600, 5= 19200, 6= 38400, 7= 57600, 8=115200, 9=230400
0x10 | 0x00B0 | 0x000204EEMMMMMM | 40176 | Float | OUTPUT. – DATA – ADDR. | Instrument address | 0..31
0x06 | 0x00B6 | 0x00XX | 40182 | List | OUTPUT. – DATA – PROT. | Communication protocol | 0=ASCII, 1=M. BUS, 2=MODBUS
0x06 | 0x00B8 | 0x00XX | 40184 | List | OUTPUT. – AN. OUT. – INP. A.O. | Input value for analog output | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x06 | 0x00BA | 0x00XX | 40186 | List | OUTPUT. – AN. OUT. – TYP. A.O. | Type | 0=0-20mA, 1=Er4- T, 2=4-20 T, 3=Er4-20, 4=4-20mA, 5=0- 5mA, 6=0- 2 V, 7=0- 5 V, 8=0-10 V, 9=+-10 V
0x10 | 0x00BE | 0x000204EEMMMMMM | 40190 | Float | OUTPUT. – AN. OUT. – MIN A.O. | Minimum display value corresponding with bottom value of selected A.O. range | -99999..999999
0x10 | 0x00C0 | 0x000204EEMMMMMM | 40192 | Float | OUTPUT. – AN. OUT. – MAX A.O. | Maximum display value corresponding with top value of selected A.O. range | -99999..999999
0x06 | 0x00C2 | 0x00XX | 40194 | List | OUTPUT. – DISP. – PERM. | Value to be permanent displayed | 0=NO, 1=CHAN. A, 2=FIL. A, 3=MAT. FN.
0x06 | 0x00C4 | 0x00XX | 40196 | List | OUTPUT. – DISP. – BRIGHT | Brightness of displey | 0= 0%, 1= 25%, 2= 50%, 3= 75%, 4= 100%
0x06 | 0x00CC | 0x00XX | 40204 | List | SERVIC. – LANG. | Language variation of menu | 0=CZECH, 1=ENGL.